# Modbus Detection Rules Document

## 1. Purpose

This document explains the purpose, structure, usage, dependencies, rule logic and timeline for implementing Modbus detection rules in the SG-X Guardian Suricata integration.

The main file for Modbus detection is:

/opt/guardian/suricata/rules/ot/modbus.rules

This file contains Suricata rules that detect risky or unauthorized Modbus activity against PLCs and industrial devices.

## 2. What is Modbus?

Modbus is an industrial communication protocol used by PLCs, HMIs, SCADA systems, sensors, and controllers.

In simple terms:

HMI / SCADA / Engineering PC

↓

Modbus command

↓

PLC

↓

Machine / motor / pump / valve / sensor system

A PLC controls machines. Modbus is one of the protocols used to communicate with the PLC.

Example actions through Modbus:

Read temperature value

Read pressure value

Write motor ON/OFF command

Write valve open/close command

Change register value

Change process setpoint

Because Modbus can be used to write values to PLCs, unauthorized Modbus commands can become a security risk.

## 3. Why Modbus Rules Are Needed

Modbus rules are needed to detect dangerous or unauthorized actions in industrial networks.

Examples:

- Unauthorized device writing to PLC coils

- Unauthorized register changes

- Safety setting modification

- PLC program or firmware upload attempt

- Too many Modbus errors from one source

- Modbus write outside allowed maintenance time

Without these rules, the system may not know that a PLC was accessed or modified by an unauthorized source.

## 4. Where Modbus Rules Fit in the Flow

The basic detection flow is:

Network traffic arrives

↓

Suricata captures the traffic

↓

Suricata detects that the protocol is Modbus

↓

Suricata parses the Modbus packet

↓

modbus.rules are checked

↓

If a rule matches, an alert is generated

↓

Alert is written to eve.json / fast.log

↓

Guardian backend can read and process the alert

## 5. How Suricata Knows Traffic is Modbus

Suricata detects Modbus traffic mainly through:

1. Port detection

2. Protocol packet structure

Modbus TCP commonly uses port:

- 502

So Suricata checks:

- Is the traffic using port 502?

- Does the packet structure look like Modbus?

- Does it contain valid Modbus function codes?

If yes, Suricata treats it as Modbus traffic and applies Modbus rules.

## 7. Main Modbus Rules to Implement

The following are the main Modbus rules that should be implemented.

### Rule 1: Unauthorized Modbus Write to PLC Coils

#### Purpose

Detect unauthorized write operations to PLC coils.

Coils are ON/OFF control points.

Examples:

- Motor ON/OFF

- Valve open/close

- Relay ON/OFF

- Alarm ON/OFF

#### Why this is risky

If an unauthorized device writes to coils, it can directly change machine behavior.

#### Example rule logic

If Modbus function is write

AND access type is coils

AND source is not trusted

THEN generate alert

### Rule 2: Write to Safety-Critical Holding Registers

#### Purpose

Detect write operations to important PLC registers. Holding registers store numeric values.

Examples:

- Temperature limit

- Pressure limit

- Speed setting

- Safety threshold

- Process setpoint

#### Why this is risky

If an attacker changes a safety register, the machine may behave incorrectly.

Example:

Normal pressure limit: 80

Modified pressure limit: 120

This could create unsafe conditions.

#### Detection condition

Modbus write function

Target is safety PLC

Register address is in critical range

#### Example rule logic

If Modbus function is write

AND register address is between 1000 and 1999

THEN generate critical alert

Note: The register range must be based on the real PLC register map.

### Rule 3: PLC Firmware or Program Upload Detection

#### Purpose

Detect attempts to upload or read PLC program/firmware data.

#### Why this is risky

PLC programs contain process logic.

Example:

- Machine start/stop logic

- Safety sequence

- Automation process flow

- Control conditions

If someone uploads or reads the PLC program, they can understand the industrial process and plan future attacks.

#### Detection condition

Modbus function code related to program or firmware upload

#### Example rule logic

If Modbus function is 65, 66, 67, or 68

THEN generate alert

### Rule 4: Excessive Modbus Exceptions

#### Purpose

Detect too many Modbus errors from one source.

A Modbus exception means the PLC returned an error response.

#### Why this is risky

Many errors from one IP can mean:

- Scanning

- Reconnaissance

- Invalid function testing

- Register range probing

- PLC fingerprinting

#### Detection condition

Too many Modbus exception responses from the same source

#### Example rule logic

If one source creates 10 Modbus exceptions in 60 seconds

THEN generate alert

### Rule 5: Modbus Write Outside Maintenance Window

#### Purpose

Detect Modbus write commands outside the allowed maintenance time.

#### Why this is risky

Industrial changes usually happen during approved maintenance windows.

Example:

Allowed write time: 06:00 to 22:00

Write at 02:00: suspicious

#### Detection condition

Modbus write command

Time is outside allowed maintenance window

#### Example rule logic

If Modbus write occurs outside the approved time window

THEN generate policy violation alert

## 8. Required Variables

The Modbus rules depend on correct Suricata variables.

Example variables:

PLC_NETWORK: "[192.168.100.0/24]"

SAFETY_PLC: "[192.168.100.20]"

ENGINEERING_STATIONS: "[192.168.100.50,192.168.100.51]"

### Meaning

| Variable | Purpose |
| --- | --- |
| PLC_NETWORK | Defines PLC IP range |
| SAFETY_PLC | Defines safety-critical PLCs |
| ENGINEERING_STATIONS | Defines authorized engineering systems |

## 9. What Modbus Rules Depend On

Modbus rules depend on the following components.

### 1. Suricata IDS Engine

Suricata must be installed and running.

Without Suricata, modbus.rules is only a text file and cannot detect anything.

### 2. Modbus Protocol Enabled in Suricata

Suricata configuration must enable Modbus parsing.

Example:

app-layer:

protocols:

modbus:

enabled: yes

detection-ports:

dp: 502

### 3. Correct Rule Path in suricata.yaml

The rules file must be included:

rule-files:

- /opt/guardian/suricata/rules/ot/modbus.rules

### 4. Real Modbus Traffic or Test Traffic

Rules only work when Modbus traffic exists.

Testing can use:

Real PLC

Modbus simulator

Modbus PCAP replay

A real PLC is not required for early development. A simulator is enough for basic testing.

### 5. PLC/OT Network Information

The rules need environment specific information:

- PLC IP addresses

- Safety PLC IPs

- Authorized engineering workstation IPs

- Critical register ranges

- Maintenance window

- Allowed commands

Without this information, the rules will be too generic.

### 6. Guardian Backend Integration

Suricata can generate alerts, but Guardian backend is needed to process them.

Backend responsibilities:

- Read eve.json

- Parse alert details

- Extract source IP and destination IP

- Extract rule ID and severity

- Create SecurityEvent

- Create ComplianceFinding if needed

- Notify admin/dashboard

## 10. Final Summary

The modbus.rules file is used to detect risky Modbus activity against PLCs and industrial systems.

Main rules:

- Unauthorized Modbus write to PLC coils

- Write to safety-critical holding registers

- PLC firmware/program upload detection

- Excessive Modbus exceptions

- Modbus write outside maintenance window

The rules depend on:

- Suricata engine

- Modbus protocol enabled

- Correct PLC network variables

- Real or simulated Modbus traffic

- PLC register map

- Guardian backend alert parser